## AS 3814 Risk assessment
AS 3814:2018
APPENDIX M
LIST OF SIGNIFICANT HAZARDS
Informative -- Adapted by E-Systems in consultation with the Tasmanian Department of Justice, Gas Standards and Safety for gas fitting risk assessment of Type B Appliances <20 GJ/hour
Table M1 lists significant, anticipated hazards together with the significant corresponding preventative measures to reduce or eliminate these hazards. organissation or person in control of the type B appliance are to cross-out any preventive measures that are not accepted. See Sections 2 to 5 of Australian Standard 3814:2018 for full details. Users are warned this is a guide only and may not be totally comprehensive or accurate for the particular need. Additional hazards may be identified by the gas fitter and/or owner and must be added to the list suggested here to manage all foreseeable risks. Particular attention is needed to address site-specific installation and operational hazards. Note that hazards suggested in Appendix M have been prioritised by the regulator. Generally, the hazards that must be assessed by the gas fitter are shown in the unshaded rows of the table below. Shaded rows indicate hazards that will generally not require assessment by the gas fitter.
Procedure: 1. Consider each hazard and decide 'How likely is this?': Will happen [expected to happen more than once a year]; Could happen [during the service life of the device being installed]; or Improbable. 2. Decide 'How serious are the consequences?': Fatality/major damage [fatality or permanent disability, a day or more to repair damage]; Injury/minor damage [lost time, off-site medical treatment, less than a day to fix damage]; or Negligible. 3. Use the risk matrix to rank the risk before considering any preventive measures that are not already part of the specifications and standards for the project. 4. Decide which suggested preventive measures will be taken, crossing-out any that will not be adopted. Write-in any other preventive measures that will be taken to reduce risk. 5. After adopting the preventive measures that are being taken, re-consider the likelihood and consequences to see if either or both factors decrease. 6. Use the risk matrix again to re-rank the risk (called 'treated risk'). If the treated risk ranking remains high, the risk is unacceptable and other preventive measures or design solutions must be considered to reduce the risk to no more than medium. This document is submitted to the regulator with the Application for Acceptance. Once the Application and risk assessment are accepted, this document is an auditable record of how the organissation or person in control of the type B appliance is managing risk for installation, commissioning and operation of the relevant gas appliances. The applicant must also provide this document to the organissation or person in control of the type B appliance for ongoing risk management, periodic review, and updating if new hazards are identified after hand-over.
Copyright © E-Systems Pty Limited, 2017. This spreadsheet tool is licensed for the exclusive use of the Tasmanian Department of Justice, Consumer, Building and Occupational Services—Gas Standards and Safety. It may be hosted electronically on the government's website or distributed as a computer file for the exclusive use of Tasmanian Type B Gas Fitters for the purpose of submitting applications for the installation and commissioning of Type B Gas Appliances <20GJ/hr. This spreadsheet tool is not authorised to be shared or transmitted in any form to third parties without the express written permission of E-Systems. Enquiries are to be directed to Richard Stoklosa, 205 Davey Street, Hobart 7000.
|  |  |  | Negligible | Improbable |  |  |  | Negligible |  | Improbable
|  |  |  | Injury/minor damage | Could happen |  |  |  | Injury/minor damage |  | Could happen
|  |  |  | Fatality/major damage | Will happen |  |  |  | Fatality/major damage |  | Will happen
TABLE M1
LIST OF SIGNIFICANT HAZARDS
|  |  |  | Based on design, installation and operating specifications and standards for gas fitting, before any preventive measures |  |  |  |  | After adopting the preventive measures
No. | Hazard (AS 3814) | Hazardous situation (AS 3814) | Description of hazard scenario | How serious are the consequences? | How likely is this? | Risk ranking | Risk-reduction measures to be considered (AS 3814) | Preventive measures —What you will actually do to reduce risk | How serious are the consequences? |  | How likely is this now? | Treated risk ranking
2 | Lack of safety studies | Devices might not function correctly under all reasonably foreseeable situations. |  |  |  |  | Risk assessment. | [5 empty] | 2.1.1.1, 2.1.1.2, 2.1.1.3
5 | Unsafe location | Appliance located in unsafe location at site, e.g. hazardous area, outdoors when should be indoors. |  |  |  |  | Designed to fit designated locations. | [5 empty] | 2.1.1, 2.1.2, 2.1.5, 2.6, 2.7, 4.2.1
6 | Inadequate design, location or identification of manual controls or visual display units | Incorrect operation. |  |  |  |  | Ergonomics. | [5 empty] | 2.1.2, to 2.1.7, 2.2, 2.6, 4.2
7 | Cutting or severing, entanglement | Fingers trapped or cut or body entanglement during maintenance activity. |  |  |  |  | Free from sharp edges. Maintenance. Adequate access for controls, burner and safety devices. | [5 empty] | 2.1.8, 2.2 2.2
9 | Burns, other injuries from contact with temperature | Contact with cold or hot surfaces of controls. Cold surfaces due to expansion of liquid to vapour. Flame radiation. |  |  |  |  | Appliance design. Warning signs. | [5 empty] | 2.4, Table 2.1, 2.3 2.4, 4.2
10 | Hot/cold surfaces | Contact with hot/cold surfaces. |  |  |  |  | Guards. Design, e.g. warning signs. | [5 empty] | 2.4, Table 2.1 2.4
11 | Damage to equipment from hot or cold environment | Equipment failure. Brittle fracture. |  |  |  |  | Material selection. | [5 empty] | 2.1.1.1, 2.1.2, 2.1.5, 2.8, 2.4, 3.4
14 | Thermal radiation | Thermal radiation from hot casings or openings affecting the safe operation of instrumentation and personnel. |  |  |  |  | Warning signs. Instructions and training. | [5 empty] | 2.1.1, 2.1.5, 2.3 2.4 4.2
15 | Falling or ejection of objects | Operator maintenance staff injured by falling objects. |  |  |  |  | Parts secured. Supports adequate. | [5 empty] | 2.1.6, 2.1.7 2.1.9
16 | Break-up— Loss of containment | Explosion. Fire. Asphyxiation. |  |  |  |  | Appliance Design. Location. Materials. Pipework design. Appliance isolating valve location. Flame safeguard. Explosion relief. No combustion product leakage. Purging. Process controls, limits and interlocks. | [5 empty] | 2.1.1 2.1.2 2.8 2.9.1, 2.9.4 2.9.8.3 2.25.2, 2.20, 2.2(d) 2.20.3.1(b), 5.10.4, 5.11.3 3.6.2, 5.4 2.20 2.21, 3.4
17 | High pressure gas or fluid injection or ejection | Over-pressure in fuel systems, instrument air supply, and process lines. |  |  |  |  | High-integrity pipework and connectors. Pressure regulation, over-pressure protection and relief. Inspection. Maintenance. | [5 empty] | 2.9.1, 2.9.4 2.10, 2.11, 2.21, 3.4 Appendix B and Appendix G 2.7, 4.2.1(g), Appendix G
19 | Poor identification of piping contents | Inability to identify piping containing dangerous media. |  |  |  |  | Identification of contents. | [5 empty] | 2.9.1
20 | Unhealthy postures or excessive effort | Hard-to-handle or use components and devices. |  |  |  |  | Adequate access to controls, etc. Appliance valve operating effort. Adequate access for maintenance. Maintenance instructions. | [5 empty] | 2.2 2.9.7.2(a) 2.7 4.2.1
22 | Mental overload and stress | Inadequate instructions and maintenance. |  |  |  |  | Training, operating instructions. Maintenance instructions. | [5 empty] | 4.2.2, 4.2.3, 4.2.4 4.2.1, 4.2.3
23 | Slip, trip and fall hazards | Falling from a height due to poor access. Standing surfaces, walkway surfaces. |  |  |  |  | Design. Access for controls, etc. Maintenance access. | [5 empty] | 2.1.1, 2.1.5 2.2 2.7
24 | Damage to equipment from environment contamination | Premature failure of appliance, burner. |  |  |  |  | Appliance location. Combustion air quality. | [5 empty] | 2.1.2 2.16.2
27 | Vibration | Adjustable devices move and affect appliance. |  |  |  |  | Design. | [5 empty] | 2.1.4
28 | Vibration | Gas-air ratio controls move out of ratio. |  |  |  |  | Design and installation. | [5 empty] | 2.28.1
29 | Vibration | Combustion instability vibration damages appliance. |  |  |  |  | Satisfactory combustion. | [5 empty] | 3.6.1(a)
30 | Vibration | Vibration of pipework, leading to failure. |  |  |  |  | Design. | [5 empty] | 2.9.1, Appendix G
31 | Vibration | Gas flexible pipe leakage or rupture on engines and turbines. |  |  |  |  | Design. | [5 empty] | 5.8.4
32 | Vibration | Fracture of exhaust or flue of engines or turbines. |  |  |  |  | Design, construction, installation. | [5 empty] | 5.8.6
34 | Asphyxiation | Asphyxiation and poisoning due to oxygen depletion or carbon monoxide by combustion product leaks from appliance, flues or exhaust. |  |  |  |  | Leakage of combustion products prevented. Exhaust stack location. No backflow from turbines or engines via other appliances. Direct fired air heaters combustion products checked. Maintenance. | [5 empty] | 3.6.2 5.8.8 5.8.7 5.7.7 4.2, Appendix G
35 | Process hazard | Process control failure. |  |  |  |  | Shutdown appliance/ burner if process operation not correct. Commissioning. | [5 empty] | 2.21 3.7
36 | Fire or explosion hazard | Gas leak in valve enclosures/ from piping. |  |  |  |  | High-integrity pipework and connectors, pressure testing. Ventilation of enclosures. Isolation of supply. Minimise sources of ignition. | [5 empty] | 2.8, 2.9.1, 2.9.4 2.9.3 2.9.8 2.10.4, 2.9.1
37 | Fire or explosion hazard | Leak of gases into the environment in potentially unsafe areas. |  |  |  |  | Location of vent terminals. Pipework integrity. Components rated for service pressure. Bleed lines safe. Gas-actuated controls bleed prevention. | [5 empty] | 2.10.5, 2.15.8, 5.4.5, 5.4.6 2.9.1 2.9.4 2.26 2.27.1
38 | Fire or explosion hazard | Gas leaking from regulator vent or safety shut-off system vent valve. |  |  |  |  | Correct venting of regulators. Correct venting of vent valves. | [5 empty] | 2.10.4, 2.10.5 2.15.8
39 |  | Over-fuelling due to regulator failure. |  |  |  |  | Over-pressure protection of regulator failure. | [5 empty] | 2.11.2 to 2.11.4
40 | Fire or explosion hazard | Over-fuelling of gas appliance on light-up. |  |  |  |  | Preventive measures. Control start flow rate. | [5 empty] | 5.8.10 3.2.3
41 | Fire or explosion hazard | Gases or vapours in the gas appliance prior to start-up. Potential for fire and explosion. |  |  |  |  | Pre-purging. Bleed lines to vent safely to atmosphere. Bleed lines to terminate at supervised burner. Bleed lines not to pass gas unless supervised burner alight. | [5 empty] | 2.20, 5.4.14.6, 5.5.5, 5.7.4, 5.8.3 2.26.1 2.26.2 2.26.2
42 | Fire or explosion hazard | Unstable or unsatisfactory combustion. |  |  |  |  | Under and over-pressure protection. Air-fuel ratio control not affect under pressure protection. Burners to maintain satisfactory combustion. | [5 empty] | 2.12.1, 2.11.3 2.28.2 3.6.1
43 | Fire or explosion hazard | Gas leakage through safety shut-off valves due to internal damage by foreign matter. |  |  |  |  | Gas supply to the appliance filtered. | [5 empty] | 2.14
44 | Fire or explosion hazard | Gas leakage through safety shut-off systems. |  |  |  |  | Redundancy in safety shut-off systems. | [5 empty] | 2.15.3, 5.8.2.1(b)
45 | Fire or explosion hazard | Gas leakage through safety shut-off systems due to premature energisation. |  |  |  |  | No energisation except for leakage detection. No bypass of safety shut-off system. | [5 empty] | 2.15.4 2.15.7
46 | Fire or explosion hazard | Explosion/fire on start or re-start. |  |  |  |  | Pre-purge. Purge sequence. Minimum purge rate. Dampers interlocked. Gas amount used at start-up. Ignition safe, reliable, smooth. Starting sequence interlocks. Ignition sequence and time controls. Manual ignition requirements. Heated oxygen sensing probes not to be source of ignition. Lockout on flame failure. One re-ignition attempt only. | [5 empty] | 2.20.1 2.20.2 to 2.20.5 2.20.2.2, 2.28.8, 5.8.3 2.19 3.2.3 2.21.1 3.2.1 3.2.2 2.22.2 2.28.9 3.5.4 3.5.5
47 | Fire or explosion hazard | Delayed ignition of main burner. |  |  |  |  | Start flame rate. Start flame proving. Main flame establishment time limited. Main flame supervision after pilot shutdown or separate supervision. Reduced start rate >5 GJ/hr. For pilot-lit large burners, slow opening safety shutoff valve. Pilot burner flame location turndown correct. Sufficient pilots for main burners. | [5 empty] | 3.2.3 3.3.1 3.3.2 3.3.3 3.3.4 2.15.5 2.23.1 2.23.2
[7 empty] | Multiport pilots light completely. Bleed lines not affect main burner. Pilot burners protected from blockage. Main burners light from each other. Line main burner sensed at furthest point from ignition. Cross-ignition satisfactory. Protected from blockage. Flame detectors to ensure cross-lighting complete. Hot surface igniters requirements. | [5 empty] | 2.23.3 2.23.4 2.23.5 2.24.2 2.24.2 2.24.4 2.24.5 2.25.12 2.25.13
48 | Fire or explosion hazard | Main flame outside combustion chamber. |  |  |  |  | Combustion to be within combustion chamber. Retractable or swivel burners—no inadvertent movement, gas leakage or incorrect position. | [5 empty] | 2.24.1 2.24.3
49 | Fire or explosion hazard | Failure to detect flame failure. |  |  |  |  | Flame safeguards certified. Comply with classification. Flame safeguard fitted. Flame detectors certified. Flame detectors to supervise separate flames if intermittent or permanent. Requirements for two flame detectors with one flame safeguard. | [5 empty] | 2.25.1 2.25.3 2.25.2 2.25.6 2.25.9, 2.25.10 2.25.11
50 | Fire or explosion hazard | Flame failure not detected soon enough. |  |  |  |  | Flame safeguard correct classification for burner and input. Maximum shutoff time following flame failure. | [5 empty] | 2.25.3 2.25.5
51 | Fire or explosion hazard | Flame safeguard fails unsafe. |  |  |  |  | Flame safeguard certified. Flame simulation to be prevented in flame detector. Flame safeguard safe start or continuous check. | [5 empty] | 2.25.1 2.25.7 Table 2.4
52 | Fire or explosion hazard | Wrong flame detected. |  |  |  |  | Flame detector not to detect another flame. | [5 empty] | 2.25.8
53 | Fire or explosion hazard | PES fails unsafe. |  |  |  |  | Safety systems. Use of AS 61508, AS 61511, or AS 62061. Certification >SIL2. Maintainable. | [5 empty] | 2.27.3, 2.27.4 2.27.4, 2.27.5.1 2.27.5.2(g) 2.27.5.2(i)
54 | Fire or explosion hazard | Fuel-rich burner air-fuel ratio. |  |  |  |  | Damper stops, secure and interlocked. Air-fuel ratio control fail safe. No unsafe variation in air-fuel ratio. Not affected by air preheat. Special requirements for PES-based systems. Pneumatic systems protected against blockage. VSDs feedback. | [5 empty] | 2.19 2.28.1 2.28.3, 2.28.5 2.28.4 2.28.6 2.28.7 2.28.8
55 | Fire or explosion hazard | Gas safety shutoff valve failure. |  |  |  |  | Strainer. Certification. Pressure of position proving/ position monitoring. More than one valve. | [5 empty] | 2.14.1, 2.14.2 2.15.1, 5.8.2.2 2.15.3, 2.15.9, 2.15.10, 5.8.2.1, 5.8.2.4 2.15.3, 5.8.2.1(b), 5.8.2.4
56 | Fire or explosion hazard | Gas explodes on startup as air too hot. |  |  |  |  | Control of gas input for air preheat temperature. AS 1375 calculation. | [5 empty] | 3.2.3.1
57 | Fire or explosion hazard | Failure of operating control or sequence. |  |  |  |  | Safety systems. No single component failure hazard. Limit device fitted. Interlock fitted. | [5 empty] | 2.27.3 2.27.2 3.4.2 3.4.1
60 | Restoration of power supply | Gas accumulation on failure. |  |  |  |  | Safe start sequence and interlocks. | [5 empty] | 3.5.1
61 | Failure of power supply | Gas release, fire, explosion. |  |  |  |  | Design. Appliance left in safe condition. | [5 empty] | 2.1.1 3.5.3
62 | Failure of safety related limit devices or interlocks | Fire, explosion, injury to personnel (eg. poisoning, suffocation) due to lack of maintenance or device unsafe failure. |  |  |  |  | Maintenance. Testing interlocks. Limites fail-safe design. Falme safeguards and detectors certified. Safety shut-off valves certified. Appliance and pilot isolating valves certified. | [5 empty] | 4.2, Appendix G 3.4.1.2 3.4.2.3 2.25.1, 2.25.6 2.15.1, 5.8.2.2 2.9.8.2(a), 2.9.10(c)
63 | Valves out of position | Uncontrolled gas or fuel supply, venting or draining of gas or fuel supply. |  |  |  |  | Position monitoring/ indication. Safety shut valves not bypassed. Alarm interlock on safety shut-off valves on shutdown. | [5 empty] | 2.15.3.6, 2.15.3.8, 2.15.4, 2.15.9, 2.15.10.5, 5.3.6.1, 5.8.2.1(b) 2.15.7 2.15.9.4
64 | Malfunction of control systems, software errors | Unexpected operating conditions. |  |  |  |  | Design. Functional safety. Commissioning. | [5 empty] | 2.1.1 2.21, 2.25.1, 2.27, 2.28 3.7
65 | Uncontrolled device operation | Protective devices do not operate as or when they should. |  |  |  |  | Manual reset of overpressure and underpressure devices. Process control protection. Testing interlocks. Limits fail safe design. Flame safeguards and detectors certified. Commissioning. |  |  | FALSE |  |  | 2.1.1, 2.12.1 2.21 3.4.1.2 3.4.2.3 2.25.1, 2.25.6 3.7
66 | Disorder of controls causing unexpected start-up | Appliance starts unexpectedly. |  |  |  |  | Start-up control and operating sequence safe. Process control protection. Limit device fitted if operating control fails unsafe. | [5 empty] | 3.4.1.1 2.21 3.4.2.1
67 | Failure/disorder of the control system | Loss of control. Uncontrolled operation. |  |  |  |  | Identification of safety-related controls. Process control protection. Damper control fails OK or lockout. Manual intervention. | [5 empty] | 2.9.5, 2.9.6, 4.1.2, 4.1.3 2.21 2.19.2.2 4.2.1, 4.2.3, 4.2.4
NOTE: Any additional hazards not included in Table M1 identified by the gas fitter, or identified by the owner or regulator for assessment.
68
69
70
71
72
73
NOTE: The following hazards are considerd lower priority by the regulator and are generally not required. However, these hazards may require assessment if special circumstances exist in the judgement of the gas fitter, or if required to do so by the regulator.
1 | Mis-application of standard | Fire/explosion/asphyxiation. |  |  |  |  | Defined scope. Desktop audits. | [5 empty] | 1.1, 1.2
3 | Combination of hazards | Hazard combinations prevent correct operation of safety devices. |  |  |  |  | Risk assessment. | [5 empty] | 2.1.1 2.1.1.1, 2.1.1.2
4 | improper use | Devices might not function correctly under all reasonably foreseeable situations. |  |  |  |  | Analysis and design. | [5 empty] | 2.1.1.3
8 | Appliance collapse | Appliance collapses, injuring operators, maintenance staff. |  |  |  |  | Appliance well constructed. Appliance supports strong enough for weight. Appliance strong enough for location. | [5 empty] | 2.1.2, 2.1.5 2.1.9 2.1.6, 2.1.7, 2.15
12 | Substances | Not suitable for gas fuel. Dangerous substances encountered during operation. |  |  |  |  | Materials of construction. Process materials. | [5 empty] | 2.1.2, 2.8 2.21, 3.4, 5.5, 5.9, 5.10
13 | Substances | Materials failing due to corrosion. |  |  |  |  | Material selection. Corrosion protection (specify type of protection). | [5 empty] | 2.8.1, 4.2.1, 4.2.3, 2.1.1.2, 2.1.2
18 | Fuel vapour lock | Rupture of pressure equipment containing dangerous goods. |  |  |  |  | Appliance design. Pipework design. Pressure relief. Over-pressure protection. | [5 empty] | 2.1.1 2.9.1, 2.9.4 2.11.3, 2.11.4 2.11, 2.21, 3.4
21 | Neglected use of personal protective equipment (PPE) | Injury. |  |  |  |  | Training. Instructions. | [5 empty] | 4.2.4 4.2
25 | Gravity, seismic loads | Structural collapse. |  |  |  |  | Design. Appliance suitable for location. Integrity of structure. | [5 empty] | 2.1.1 2.1.2 2.1.5, 2.1.9, 4.2.1
26 | Wind | Collapse of appliance. Unsafe combustion. |  |  |  |  | Appliance suitable for location. Strength of supports. Combustion requirements. Maintenance. | [5 empty] | 2.1.2 2.1.9 3.6, 4.2.1 Appendix G
33 | Pollution | General pollution hazard from an afterburner. |  |  |  |  | Other authorities requirements. | [5 empty] | 5.5.2.1(Note)
58 | Overpressure ejection | Failure of pipework or pipe components, valves. Reverse flow. |  |  |  |  | Design. Pressure rating of components. Protection device reverse flow. Pressure rating of safety shut-off valves. | [5 empty] | 2.1.1 2.9.1, 2.9.2, 2.9.3 2.9.5 2.15.6.1
59 | Errors made by the operator | Absence or incorrect fitting causing injury or death. Human factors leading to incorrect assembly of critical parts. Human factors leading to guards missing. |  |  |  |  | Design. Electrical connection assembly features. Training/competence. Risk assessment. Permit to work. Instructions. Limits of safe operation specified. Markings on parts, controls. | [5 empty] | 2.1.1 2.5 4.2.4 2.1.1.1 3.4.1 4.2.1, 4.2.2 4.2.3 4.1.2, 4.1.3

## Risk matrix
Likelihood | Consequences
| Fatality, major damage | Injury, minor damage | Negligible
1 | High | High | Low
2 | High | Medium | Low
3 | Medium | Low | Low
Consequences | Likelihood |  |  | Consequences | Likelihood
| Will happen | Could happen | Improbable |  | Will happen | Could happen | Improbable
1 | High | High | Medium | Fatality, major damage | High | High | Medium
2 | High | Medium | Low | Injury, minor damage | High | Medium | Low
3 | Low | Low | Low | Negligible | Low | Low | Low